Draft

Code of Practice

for

Avoiding Danger from Underground Services

HEALTH AND SAFETY AUTHORITY

DRAFT

CODE OF PRACTICE FOR

AVOIDING DANGER FROM UNDERGROUND SERVICES

FOREWORD

The Health and Safety Authority (by virtue of Section 60 of the Safety, Health and Welfare

at Work Act 2005), following public consultation and with the consent of ……….., Minister of State at the Department of Enterprise, Trade and Employment, has issued a Code of Practice entitled “Code of Practice for Avoiding Danger from Underground Services”.

The Code of Practice provides practical guidance as to the observance of Part 5 of the Safety, Health and Welfare at Work (Construction) Regulations 2006 (S.I. No. 504 of 2006) which, inter alia, require that adequate precautions are taken in any excavation, shaft, earthwork, underground works or tunnel to avoid risk to persons at work arising from possible underground dangers such as underground cables or other distribution systems, the circulation of fluids or the presence of pockets of gas, by undertaking appropriate investigations to locate them before excavation begins. The Code of Practice also provides practical guidance as to the observance of Sections 19 and 20 of the Safety, Health and Welfare at Work Act 2005 in respect of relevant excavation work.

The aim of the Code of Practice is to improve the level of safety with which excavation work is carried out. In particular, it aims to reduce the incidence of damage to underground services and in doing so to minimise risk to personnel who are involved in carrying out this work.

This Code of Practice comes into operation on ……………….. 2009 and from that date it replaces the Code of Practice entitled ““Code of Practice for Avoiding Danger from Underground Services” which was issued by the Authority in February 2005 in accordance with the Safety, Health and Welfare at Work Act 1989.

Notice of the issue of this Code of Practice was published in the Iris Oifigiuil of … 2009.

Robert Roe

Assistant Chief Executive and Secretary to the Board

TABLE OF CONTENTS

| 1.0 | Introduction | 7 |
| --- | --- | --- |
| 2.0 | General | 8 |
| 3.0 | Role of the client | 10 |
| 4.0 | The role of the project supervisor appointed for the design process |  |
|  | (PSDP) and designers | 11 |
| 5.0 | The role of the project supervisor construction stage, contractor |  |
|  | and utility/services provider | 13 |
| 6.0 | Safe system of work | 14 |
| 7.0 | Use of plans in the preparation of projects | 16 |
| 8.0 | Cable and pipe-locating devices | 18 |
| 9.0 | Safe digging practice | 20 |
| 10.0 | Safe systems of work for trenchless methods | 23 |
| 11.0 | New housing developments | 24 |
| 12.0 | Installation of new services near existing services | 25 |
| 13.0 | Demolition sites | 26 |
| 14.0 | Training | 27 |
| 15.0 | Notes on appendices | 30 |

| Appendices |  |  |
| --- | --- | --- |
| Appendix 1 | Electricity cables | 32 |
| Appendix 2 | Gas pipes | 38 |
| Appendix 3 | Water pipes and sewers | 45 |
| Appendix 4 | Suggested job aid for workers on a safe system of work |  |
|  | for digging | 46 |

1.0	Introduction

1.1 Background

This Code of Practice replaces the Code of Practice of the same name published in 2005 and which was the result of a joint initiative between the Health and Safety Authority, Construction Industry Federation, Irish Congress of Trade Unions, key utilities companies/service providers and local authorities that are involved in the provision and maintenance of vital underground services such as electricity, gas and water. This Code of Practice takes into account legislative changes in the meantime in the Safety, Health and Welfare at Work Act 2005 and the Safety, Health and Welfare at Work (Construction) Regulations 2006.

The aim of the Code of Practice is to improve the level of safety with which excavation work is carried out. In particular, it aims to reduce the incidence of damage to underground services and in doing so to minimise risk to personnel who are involved in carrying out this work.

1.2 Status of the Code of Practice

This Code of Practice is published by the Health and Safety Authority under Section 60 of the Safety, Health and Welfare at Work Act 2005 and with the consent of the Minister of State at the Department of Enterprise, Trade and Employment.

The Code is intended to provide practical guidance to utility companies, clients, designers, planners, project supervisors (both design process and construction stage), safety representatives and any personnel who are involved in carrying out work where personnel are at risk from underground services.

1.3 Scope of the Code of Practice

This Code of Practice gives recommendations and practical guidance on how to carry out excavation work safely in the vicinity of underground services. In this context “excavation” means any work that involves penetrating the ground at or below surface level.

Excavation carried out in the vicinity of underground services includes work associated with a new or existing building, which may involve the risk of damaging underground services. It encompasses all excavation work carried out on roadways, streets, footpaths and other open areas where there is a likelihood of buried underground services.

The Code also contains guidance on how to prevent future damage to services that are currently being installed.

2.0	General

2.1 Introduction

Electrical cables, gas pipes, water pipes and sewers, if damaged may pose a direct danger to personnel who are working on the site. Damaged telecommunications cables may also be hazardous, although direct risk of personal injury is rare.

2.2 Electricity cables

Injuries that result from damage to live electricity cables are usually caused by the explosive effects of arcing current and by any associated fire or flames that may follow when the sheath of a cable and the conductor insulation are penetrated by a sharp object such as the point of a tool, or when a cable is crushed severely enough to cause internal contact between the sheathing and one or more of the conductors.

Typically, this causes severe and potentially fatal burns to the hands, face and body. Some high voltage electricity cables (e.g. 38kV and higher voltage) are filled with oil and, if damaged, the oil may auto-ignite and create an explosion or fire. Direct electric shock is rare but not impossible.

Incidents may also arise from cables that have been damaged, but have not been reported

to the relevant service provider and, therefore, have not been repaired. In such circumstances nearby services such as plastic gas pipes may be at risk from damaged live electricity cables, which could create explosions or increase fire risk.

2.3 Gas pipes

Damage to gas pipes can cause leaks which may lead to fires or explosions. There are two types:

(i)	damage that causes an immediate leak following a pipe rupture, and

(ii)	damage that causes a leak some time after the event. For example, damage to

a pipe wrapping may occur while work is being carried out and this damage may eventually lead to corrosion. Damage may also occur after the work has been carried out. For example, poor reinstatement may leave a pipe inadequately supported or subjected to unequal forces.

In the case of the former type of damage, those most likely to be at risk are personnel who are carrying out the work and others in the immediate vicinity. In the case of the latter type

of damage, those most likely to be at risk are members of the public.

2.4 Water pipes and sewers

While damaged water pipes are less likely to cause an injury, a jet of water emanating from a high-pressure main could injure people or damage adjacent underground services.

In addition, a water leak from an underground pipe could wash away subsoil, thereby reducing support for adjacent services, roads and structures. Additional dangers include the risk of flooding trenches or low-lying areas such as nearby basements.

Sewers are generally gravity fed, but some sewage is pumped at pressure. While the main risk to people associated with damage to sewers is the possibility of contamination, these pipes may also emit gases such as methane. At certain concentrations methane may be flammable.

2.5 Telecommunications cables

Although damage to telecommunications cables may be very expensive, there is normally no direct risk of personal injury.

2.6 Accumulation of gases

Flammable and toxic gases may escape into cable-carrying ducts, particularly if ducts have been damaged. Such gases may accumulate in chambers and manholes and may pose a risk

to personnel who are carrying out work in these areas.

3.0	Role of the client

3.1 Introduction

A “client” is defined as a person or organisation on whose behalf a construction project

is carried out. Under the Safety, Health and Welfare at Work (Construction) Regulations, the  client  must  appoint  a  competent  project  supervisor  design  process  (PSDP)  and  a competent project supervisor construction stage (PSCS) for every construction project.

3.2 Information from clients

Clients or their agents have a duty to pass on any relevant information relating to underground services that may be in their possession to the PSDP or the PSCS. This information should be as up to date as possible. The client should also make available a copy of any safety file that  is  relevant  to  the  construction  work  that  is  about  to  be undertaken.

3.3 Other duties

In accordance with Section 12 of the Safety, Health and Welfare at Work Act 2005, it is the duty of each person (or company) who has control to any extent of any place of work, or any part of a place of work, to take such measures as are reasonable for them to take, to ensure so far as is reasonably practicable that the place of work is safe and without risk to health. In certain cases, this provision may be applicable to clients who commission projects that will involve carrying out excavation work near underground services. Section 17 of the Act specifies duties to be complied with by persons who commission or procure construction work. Such persons must appoint in writing a competent person or persons to ensure, so far as is reasonably practicable, that the project is designed and is capable of being constructed to be safe and without risk to health,

4.0	The role of the project supervisor appointed for

the design process (PSDP) and designers

4.1 Definition of designer

The term “design” covers the preparation of drawings, design details, specifications and bills of quantities. A “designer” is defined as any person who is involved in such work.

4.2 The project supervisor design process

All designers’ work should be co-ordinated by a project supervisor for the design process (PSDP). The PSDP has a duty to prepare and provide to the project supervisor for the construction stage (PSCS) a preliminary safety and health plan if the project is expected to last more than 30 days/500 person days, or if it contains a “particular risk”, as defined in the Safety, Health and Welfare at Work (Construction) Regulations. One such “particular risk” is working near high-voltage power lines: this includes both overhead lines and underground cables.

The preliminary safety and health plan must contain an overall description of the project,

its proposed timescale and appropriate information relating to other work on site. It must also specify any work related to the project that will involve “particular risks”.

Unforeseen circumstances may arise during the execution of the project, which may result

in a design change. This may in turn have safety, health and welfare implications. The PSDP has a duty to direct the designers in relation to the safety, health and welfare implications of any change in the original design.

The PSDP must prepare a Safety File for the project and present it to the client when the project is complete.

4.3 Use of plans during design

Where possible, the designers should obtain up-to-date maps and records of all potentially hazardous underground services in order to allow them consider, at the design stage, the risks posed by those services. Plans and maps should be made available to prospective contractors at tender stage or contract negotiation stage. Before beginning any work on

a site, the contractor should be satisfied that the drawings supplied contain the most up-

to-date information available for the area in which the works are to be carried out.

4.4 Underground services and building work

4.4.1	Relocating   underground   services   some   distance   away   from   the   proposed construction site may provide a reasonably practicable means of avoiding the risk of causing damage to these services. Any requests for the relocation of services should allow for sufficient time for the relevant utilities’ providers to evaluate such proposals and carry out their work.

Buildings and other permanent structures should not be erected over underground services

because this may create additional risks for construction workers and could prevent future access  to  those  services.  If  it  is  not  possible  to  avoid  erecting  a  structure  over  an underground service, arrangements should be made with the relevant utility provider to relocate the service if this is practicable.

4.4.2 Other options to resiting the services may include:

•   repositioning  structures  or  parts  of  structures  to  ensure  that  contact  with underground services is avoided while the work is being carried out

•   arranging  for  the  supply  contained  within  the  underground  services  to  be disconnected during the work.

If neither of these options is possible, then choosing methods to avoid contact, such as using ground beams to protect the service(s), may present a reasonably practicable option.

4.4.3 Designers should take into account any ancillary work that may be required including the  erection  of  perimeter  fencing  and  walls,  or  the  construction  of  roadways.  Early identification and planning are essential if risks are to be controlled.

4.4.4 Where new services such as electrical or gas supplies are being installed, it may be possible to reduce risks by not installing or commissioning these services until other ground works and installation works have been completed.

4.5 Underground services in paths and roadways

4.5.1 The options facing designers who are planning a new service in a roadway may be more limited. In order to select a route that avoids contact with existing services, it is important to have access to the most up-to-date information about those services. One option is to choose a route that has a low density of underground services. For example,

a cable television duct might be routed at the side of a road, if that site has a reduced cable density. Designers of gas pipelines should also be aware of the guidance contained in IS328: 2003 Code of Practice for Gas Transmission Pipelines; IS265 2000 Installation of Gas Service Pipes and IS329 2003 Code of Practice for Gas Distribution Mains.

4.5.2 Having reduced the risks to a level as low as is reasonably practicable by design, information should be provided by the designer(s) about the risks which remain. In most cases the best way of informing those physically excavating in the vicinity of underground services is by providing the information on drawings, ensuring that the information given

is the best available.

5.0	The role of the project supervisor construction

stage, contractor and utility/services provider

5.1 Project supervisor construction stage (PSCS)

The role of a project supervisor construction stage (PSCS) is to coordinate  the project from

a health and safety perspective. The PSCS must also develop the safety and health plan, which should outline how the management of the safety, health and welfare of on-site personnel is to be achieved. In addition, the PSCS must facilitate safe access to the site and

co-ordinate the overall implementation of safe working procedures.

5.2 The contractor

All contractors must carry out a site-specific risk assessment. They should also ensure that their employees have adequate training and that any plant or machinery is, so far as is reasonably practicable, safe and does not pose a risk to health. They should also put in place measures to ensure that the health and safety of personnel who are employed by them are not adversely affected by work being carried out by the contractor.

Sections 6 to 13 of this Code set out practical measures by which the safety, health and welfare of employees and non-employees may be protected while excavation work

is being carried out in the vicinity of underground services.

5.3 Utilities

Utility/service providers such as local authorities, Bord Gáis and the ESB own most of the underground services, which, if damaged during excavation work, may pose a danger to contractor personnel. For that reason, utility/service providers should ensure that their records and maps are maintained as accurately as possible. They should make these records readily available to designers and contractors, as appropriate. (See Section 7.3).

In circumstances where a utility company is asked to provide permanent services for a building development, that company will be acting in the role of contractor. Therefore, while it is on site, it will be required to comply with any directives given by the PSCS. However, in circumstances where the provision of services is physically separated and demarcated from the site, then the utility company may assume the role of client for the purposes of the Safety, Health and Welfare at Work (Construction) Regulations.

6.0	Safe system of work

6.1 Introduction

Underground utilities networks are a common feature in both rural and urban areas and their presence should be assumed until proved otherwise.

The guidance given in this Code aims to minimise the possibility of risk to personnel who are involved in work that exposes them to contact with underground networks. It sets out

a safe system of work that is based on obtaining as much information as possible about buried services before excavation work begins and using that information to ensure that the work is carried out safely.

6.2 Basic elements

In the context of this Code, a safe system of work is defined as having three basic elements:

(i) Plans

Plans or other suitable information about all buried services in the area should be obtained before excavation work begins (see Section 4 on “The Role of the Designer” and Section

7.4 on “Use and Limitations of Plans”). This material should be passed on as early as reasonably practicable by the designer through the project supervisors to the contractor who is tendering for, or is negotiating the carrying out of, the works.

Plans that were used at the design stage and at the tendering stage may have gone out

of date by the time excavation work begins. Therefore, before beginning any such work, the contractor should check that the plans supplied are the most up to date available.

Account should also be taken of possible indications of the existence of underground services such as the presence of houses or other buildings, lamp posts, illuminated traffic signs, pit covers, evidence of reinstated trenches and so on. However, the absence of such indications does not necessarily indicate that underground services do not exist.

(ii) Cable and pipe-locating devices

Suitable cable and pipe-locating devices should be used in conjunction with any available plans to determine as accurately as possible the position of metallic underground services

in or near the proposed work area. It should be noted however that these devices do not detect plastic pipes (see Section 8).

(iii) Safe digging practices

Excavation work should be carried out carefully and should follow recognised safe digging practices (see Section 9).

These key elements – plans, locators and safe digging – complement each other and all three should be used when working near buried services. Using one element alone may not be enough.

6.3 Employees

Employees should receive adequate instruction and training in the above procedures (see Section 14 on Training). A suggested job aid for workers’ information is set out in Appendix 4. It is particularly important that anyone who is using a locator should have received thorough training in the use and limitations of that particular type or model of device. Most manufacturers will provide such training, and employers should ensure that this is adequate for their employees’ needs.

6.4 Procedures

The organisation and arrangements necessary for avoiding danger from exposure to underground services should form part of employers’ statutory safety statements. Written site-specific risk assessments of the work being undertaken should also be carried out.

7.0	Use of plans in the preparation of projects

7.1 Introduction

Up-to-date plans of all potentially hazardous underground services in the area should be obtained before  excavation  work  begins.  Where possible,  providers  of  all  relevant underground services should be consulted. It should be noted that, for certain types of utilities, there may be more than one service provider in a particular catchment area. For example, while most electricity cables under roads and other public areas are owned by the ESB, many electricity cables are the property of local authorities and are used for providing services such as public lighting, traffic lights and so on.

7.2 Emergency works

In the case of emergency* works it may not be possible to obtain all requisite up-to-date plans prior to beginning excavation work. In such situations, all other aspects of safe digging practice should be complied with (see Section 9) and the work should be carried out in the same manner as if there were underground services on the site.

7.3 Availability of plans from service providers

7.3.1 Utility or service providers should make available either up-to-date, readable plans that show the recorded line and depth (where known) of all underground services in the proposed work area, or they should provide other suitable information that achieves the same objective. The inclusion of a symbol key will generally be necessary to help the recipient understand the plans.

7.3.2 Utility or service providers should do everything that is reasonably practicable to ensure that such information is made available to enquirers. They are likely to receive many routine applications for information and they should consider how best to make this information available at short notice. In cases where utility or service providers have reservations about releasing copies of plans, for commercial/security reasons, they should offer an alternative method of co-operation. For example, send a representative to the site

to communicate the requisite information to designated contractor personnel only.

7.4 Use and limitation of plans

Plans vary in scale, content and style and adequate instruction and training in how to read and interpret them should be given to anyone who needs to use them.

–––––––––––––––––––––––––––––––

* If the question arises in criminal or civil proceedings as to whether or not works were emergency works, it

is for the person alleging that they were to prove that this was the case. Clients and contractors should not use “emergency work” work as an excuse to justify a failure to plan properly when starting work without plans or other suitable information about underground services in the area.

Plans may give an indication of the location, configuration and number of underground

services on a particular site. However, they are rarely drawn accurately to scale and, even

if they claim to be accurate, they should not be relied upon in order to obtain accurate distance  measurements.  Errors  may  have  been  made  during  the  drafting,  or  the reproduction process may have altered the scale of the plan, particularly if the original data was obtained from a microfiche slide or a digital map. Accuracy may be further limited because:

•	the position of reference points (e.g. the kerb line) may have changed since the plans were prepared originally

•	the regrading of a particular surface area may mean that the depths shown on the plan are no longer correct

•	fixtures such as cables, may have been moved without the knowledge of the utility/service provider

•	in many cases service connections are not marked

•	services that appear as straight lines on a map may, in fact, be laid out in a snake- like formation; excessively long cables may have been laid in horizontal loops outside substations and switch rooms

•	plans may show spare ducts; and

•	the routes of older services in particular may not have been recorded and so the absence of records should never be taken as proof that the area in question is free of underground services.

8.0	Cable and pipe-locating devices

8.1 Position of services

The position of any services in or near the proposed work area should be pinpointed as accurately  as  possible  by  means  of  a  locating  device.  This  device  should  be  used  in conjunction with plans and other relevant information (see Section 8.2(a)) as a guide to the possible location of services and to help interpret the signal.

8.2 Types of locating devices

The main types of locator available may be classed as follows:

a)	Hum detectors (e.g. a cable-locating device set on power mode) are receiving instruments that detect the magnetic field radiated by live electricity cables, which have a current flowing through them. However, these instruments will not detect service connection cables to unoccupied premises or street lighting cables during the daytime, as little or no current will be flowing through the cables at that time. They may also fail to detect some well-balanced high-voltage cables, where these cables generate little magnetic field. (It should be noted that the absence of current

in a live cable does not in any way alter the risk of injury to a person if the cable is damaged).

b)   Radio frequency detectors (e.g. a cable-locating device set on radio mode) are receiving instruments that respond to low-frequency radio signals, which may be picked up and re-emitted by cables and long metallic pipes. If radio frequency detection is used, other metallic objects may re-radiate the signal and results may vary appreciably according to locality, length of the buried cable or pipe, distance from the termination and geographical orientation.

c)	Transmitter-receiver   instruments:   With   these   instruments   a   small   portable transmitter or signal generator is connected to a cable or pipe, or placed very close

to it, so that the signal is induced into it. The receiver then detects that signal. Usually, some part of the cable or pipe will need to have been located in advance

of the operation in order to ensure that the transmitter is positioned correctly. Transmitter-receiver instruments generally require more skill to operate than other types  of  locators.  They  may,  however,  provide  useful  information  in  difficult situations where using locator equipment such as (a) and (b) above has not proved successful. In addition, they can provide a depth-measuring facility.

d)   Metal detectors: Conventional metal detectors will usually locate flat metal covers, joint boxes and so on, but may well miss round cables or pipes. They can be a useful tool for finding inspection points. These inspection points may themselves provide connection points for a transmitter for use of transmitter-receiver instruments.

Most commercially available instruments use more than one of these techniques and may also include a depth-measuring facility.

8. 3 Locating the service

The degree of confidence with which buried services may be detected depends on a number of factors such as the characteristics of the devices being used; the type and depth

of the service; the magnitude of the current carried by the cable; the effects of other cables and metal pipes close by; the training, skill, hearing and experience of the operator.

In particular, a locator may not be able to distinguish between cables or pipes running close together and may represent them as a single signal. If two cables or pipes are sited one above the other, it may not detect the lower one. For that reason, frequent and repeated use of the locator should be made during the course of the work.

With the possible exception of ground-probing radar, locators will not detect plastic pipes

or other non-metallic ducts and services unless:

a)	a  metallic  tracer  wire  has  been  laid  with  the  pipe.  This  enables  a  signal transmitter/receiver to be used. Plastic gas and water pipes are the most likely type of non-metallic pipe to be encountered and some of these pipes may have been laid with metallic tracer wires.

b)	a small signal transmitter is inserted into and then pushed along the pipe. This

is a sophisticated technique and is not likely to be appropriate for many sites.

Locating devices should always be used in accordance with the manufacturers’ instructions. They should be checked regularly and maintained in good working order. The line of any identified services should be noted and marked with waterproof crayon, chalk or paint on paved surfaces. Any residual markings should be erased after excavation as far as possible.

On grassed or unsurfaced areas, wooden pegs should be used. Steel pins, spikes or long pegs, which could damage services laid at shallow depth, should not be used.

Important Note.

Construction Skills Certificate Scheme (CSCS)

The Safety Health and Welfare at Work (Construction) Regulations 2006 requires persons carrying out the task of Locating Underground Services to be in possession of a CSCS card. This is dealt with in more detail in Section 14 Training.

9.0	Safe digging practice

9.1 Excavating

Once plans and a locator device have been used to determine the position of underground services, excavation may proceed. This work should be carried out carefully, following recognised safe digging practices. Trial holes should be dug using hand tools to confirm the position of any buried services. Special care should be taken when digging above or close to the assumed lines of any such services. Hand-held power tools are the main source

of danger to personnel and they should not be used too close to underground services. (See Appendices (i) and (ii) for advice on appropriate safety margins for electricity and gas respectively).

Hand tools, incorrectly used, are a common cause of accidents. However, if they are used carefully and if the approximate position of services has been determined through the use of plans and locators, these tools may provide a satisfactory method for exposing underground services. Every effort should be made to excavate alongside the service rather than directly above it. Final exposure of the service by horizontal digging is recommended

as the force applied to hand tools may be controlled more effectively.

In particular:

(a)	Spades and shovels should be used rather than other tools. They should not be thrown, or spiked into the ground. Rather, they should be eased in with gentle foot pressure;

(b)	Picks, pins or forks may be used with care to free lumps of stone and other materials and to break up hard layers; and

(c)	Picks should not be used in soft clay or other soft soils in areas close to buried services.

Particular care should be taken in cases where gas leak search techniques such as barholing are used. Refer to Bord Gáis Éireann guidance material for advice.

9.2 Damaged services

If an underground service suffers damage, no matter how slight, the utility or service provider should be informed immediately. In the case of electricity cables, gas pipes or high-pressure water mains, arrangements should be made to keep personnel well clear

of the area until it has been repaired or otherwise made safe by the utility or service provider.

9.3 Identification of services

Failure  to  identify  underground  services  correctly  could  cause  an  accident.  Correct identification may prove difficult as the utility or service providers may have used a wide variety of materials and colours over a number of years. It is important to remember that colours may appear differently under poor or artificial lighting. In addition, ducts may well contain any one of a number of services, irrespective of the type or colour of the duct. Some services are very similar in appearance and the following approaches should be adopted until such time as their identity has been positively confirmed:

(a)  The housing for some water pipes, electricity cables and telecommunications cables may be made from black plastic. If a black plastic-covered service is encountered,

it should be assumed to be a live electricity cable until proved otherwise.

(b)  Iron and steel water pipes may look very similar to gas pipes. Therefore, if any iron

or steel pipe is uncovered, it should be handled as if it were a gas pipe.

(c)   Some services run in ducts, which may make these services difficult to identify.

Where red ducts are uncovered, the services inside those ducts are likely to be electricity cables of modern installation and they should be treated as such. Where yellow ducts are uncovered, they are likely to be gas pipes and should be treated

as such. Black and orange ducts have been used as standard colours for electricity cables in the past and they should be handled as if they contained electricity cables.

(d)  Electricity cables may also be installed in concrete pipes, steel pipes and in plastic ducts in a range of colours. Where there is any doubt about the identity of an exposed service, it should be treated as if it were an electricity cable or gas pipe until proved otherwise.

Ducts for electrical cables (wherethe cable voltage exceeds 125V) should be coloured

red in accordance with Appendix 1

All cables should be assumed to be live until disconnected and proved safe. Contractors

should either obtain written confirmation of disconnection from the service provider before removing a redundant service or they should arrange for the service provider to remove the service.

9.4 Support to exposed services

Services uncovered in an excavation may need to be supported and should never be used

as handholds or footholds by personnel when climbing out of an excavation.

9.5 Back-filling

Back-filling of any excavation should be carried out carefully. Where possible, any warning tiles, bricks, tapes and so on that are lying above the services should be replaced in their original position unless an expert adviser confirms that the original position was incorrect.

If the original position turns out to have been incorrect, then the warning tiles and other materials should be placed above the services to which they refer.

Warning tape should not be used for any other purpose such as guarding an excavation

trench. Neither should the tape be left in the excavation area when it is back-filled.

Fill material that contains items such as large pieces of rock and hardcore should not be used as this could cause damage to the services.

For specific advice on back-filling in the vicinity of gas pipes (i.e. where long-term damage

is  a  particular  hazard)  see  Appendix  (ii).  Alternatively,  utility  providers  may  provide direction  and  advice  on  how  to  back-fill  trenches  in  which  their  services  have  been exposed.

9.6 Burial of existing services

If underground services have been found to be too shallow, or if the plans or other information have proved to be inaccurate, the relevant utility or services provider should

be informed – preferably before the excavation is back-filled. The utility or service provider should then amend their records accordingly.

9.7 Protection against burns

Burns are the main injuries that result from damage to live electrical cables, or from fire

or explosion following a gas leak. In many cases a burn will be more severe if the injured person is working bare-chested.

While the wearing of ordinary work clothing may greatly reduce the severity of a burn, the wearing of protective clothing may be a more effective measure. However, clothing made from man-made fibres such as nylon may melt and adhere to the skin, thereby increasing the severity of burns. The wearing of protective clothing should never be used

as a substitute for a safe system of work.

(For further advice on the types of clothing that should be worn when working near electricity cables see Appendix 1).

9.8 Insulated digging tools

Where excavation work is being carried out near live cables it will generally be necessary

to use insulated hand tools. Generally, tools such as shovels, spades or picks should have insulated fibreglass or wooden handles. Fibreglass crowbars are also available and these should be used where feasible. If this is not feasible, then the crowbars should be fitted with insulated handles.

10.0 Safe systems of work for trenchless methods

Increasingly,  trenchless  methods  are  being  used  for  the  laying  or  renovation  of underground pipes and cables, particularly in cases where it is necessary to avoid disturbing surface areas. The most widely used techniques are impact-moling, pipe-bursting and auger-boring. Care should be taken when using trenchless methods to avoid colliding with and, thereby, damaging other services. With moling and pipe-bursting it is also important not to work too close to other services as displaced soil may escape into nearby pipes or ducts.

Plans, locators and trial holes should be used to determine the position of existing services. The path of the equipment to be used should then be calculated accordingly. In order to avoid danger and allow sufficient clearance for the maintenance of existing services, the general guideline is that the minimum clearance between adjacent services should be either 250mm or one and a half times the diameter of the pipe being laid, whichever is the greater. For electricity cables, clearances for maintenance work should be approximately

300mm.

In certain circumstances, clearances may need to be varied. Therefore, contractors should take into account factors such as the construction of adjacent plant; ground conditions; bore diameter; the accuracy and reliability of the technique/equipment being used and whether  the  other  plant  is  parallel  or  crossing  the  proposed  line.  In  addition,  the requirements of nearby utility/service providers may need to be taken into account.

Moles are prone to deflection from their original course and if there are existing services

in the vicinity, a mole-tracking device should be used. Where trenchless methods are being used,  all  equipment  should  be  earthed  at  all  times.  As  an  additional  precaution,  an equipotential mat could be used in case the equipment strikes a power cable and this causes it to become live.

11.0	New housing developments

Underground  services  that  are  located  within  the  confines  of  partly  completed  new housing developments are especially prone to damage from the numerous site operations that may need to be carried out.

The construction of a single trench may help to control the position and separation of underground  services.  Where  services  are  laid  on  a  partly  developed  site,  special arrangements may be required for their temporary protection at vehicle/plant crossing points.

Close liaison should be maintained between the developers, their contractors and the utility  or  service  providers.  A  marked-up  plan  of  the  estate,  showing  the  up-to-date position of underground services (including any variations from planned routes) should be kept on site.

12.0 Installation of new services near existing services

New underground services often have to be laid in ground that contains pre-existing services. Where it is reasonably practicable to do so, the utility/service provider that is planning the new installation should aim to position it in such a way that it is separated from all existing underground services by an adequate distance. Guidance on the requisite distances to be maintained may be found in the UK publication National Joint Utilities Group (NJUG) Guidelines on the Positioning and Colour Coding of Underground Utilities’ Apparatus. Every effort should be made to comply with this standard (unless otherwise noted in this code), or other equivalent standards of good practice for new installations, in order to minimise risk to personnel now or at some future date.

In circumstances where it is not possible to comply with the recommended standard, because of underground services congestion or some other factor, as great a separation

as is reasonably practicable should be maintained.

Where the installation of a new service is likely to obstruct access to an existing service for more than a few metres, then all reasonably practicable measures should be used to avoid this situation. In particular, the practice of laying multiple ducts directly above other services should be avoided.

Where the utility provider that is laying the new underground service has had to reduce the separation distance, they should inform every other utility provider whose service has been affected. This will enable them to amend their records for future reference.

13.0 Demolition sites

Special difficulties may arise in the case of service terminations in a derelict property or on

a demolition site.

Contractors who plan to engage in demolition work have a duty to give adequate notice

to the relevant gas, electricity and water authorities of their intention to carry out this work. Demolition should not begin until the relevant authorities have confirmed in writing that the supply has been disconnected, or some other appropriate safeguarding action has been taken.

As noted in Section 4.3, there is an onus on the PSDP who is co-ordinating the design team

to identify hazards associated with the existing environment including known hazardous underground services.

Underground services on industrial or commercial sites may be the property of the site occupier. A contractor who is planning to demolish buildings or plant on such a site should contact the site occupier or the site owner to ensure that all relevant services are isolated before demolition work begins.

Even where supplies have been disconnected, contractors should be aware that:

(a)	Services that run through a site may not be providing a service to that site.

(b)	Bottle-ended or pot-ended cables must be treated as live unless confirmed otherwise.

(c)	Some  services  may  not  have  been  recorded  on  the  original  plans  and, consequently, may not have been identified or disconnected.

14.0 Training

14.1 Introduction

Digging close to underground services is potentially dangerous. Both the workers and the supervisors who are involved in this activity need an appropriate level of knowledge, skills and experience in order to ensure that the work is carried out safely. Anyone who does not possess these attributes should work under the close supervision of someone who does have the requisite experience and competencies.

14.2 Training for supervisors and operatives

In accordance with the Safety, Health and Welfare at Work (Construction) Regulations, operatives  must  satisfactorily  complete  the  one-day  Safe  Pass  safety awareness   programme. However, this is an introductory course in construction safety and does not in itself provide sufficient  training  in  relation  to  the  hazards  and  risks  involved  in  digging  close  to underground services.

Personnel  who  are  routinely*  involved  in  either  the  supervision  or  carrying  out  of excavations in the vicinity of hazardous underground services should be trained in the following areas:

a)	Planning of the work b)	Legislation

c)	Risk assessment

d)	Liaison with utility providers

e)	Use of plans and drawings from the various utility providers

f)	Identification of services

g)	Cable and pipe-locating devices h)	Appropriate use of these devices

i)	Safe digging

j)	Personal protective equipment.

Formal refresher training will be required periodically depending on the work being carried out by personnel.

* These include workers who manually work on excavations in streets, utility or service provider employees

who manually work on excavations and those directly supervising these workers. Excavator drivers may be excluded if they have received sufficient relevant training on an excavator driving course. However, if they are involved in excavation outside the excavator, they should receive the stipulated training.

Employees should not refuse reasonable offers of training; they should cooperate with

their  employers  regarding  training  and  they  should  make  relevant  documentation demonstrating receipt of training available for inspection as appropriate.

14.3 Site based direct managers/supervisors

Those involved in direct management and supervision of site-based work require relevant competencies to deliver safety standards on site. They will need health and safety training

in order to:

•	assess and prioritise the risks on a particular project;

•	design safe systems of work that are appropriate to specific site conditions;

•	prepare  clear,  simple  safety  method  statements  that  can  be  used  and understood by site workers;

•	check that appropriate personal protective clothing and equipment has been provided and is being used correctly.

14.4 Role of the project supervisor construction stage in training

As part of their duty to coordinate  site safety, the PSCS must have a system in place for checking that on-site operatives have been appropriately trained, even if those operatives are not employees of the PSCS. The PSCS should have a system in place for ensuring and that all craft and general construction workers on site have an up-to-date Safe Pass card and appropriate Construction Skills Certification cards where required.

14.5 Construction Skills Certificate Scheme (CSCS)

The Construction Skills Certificate Scheme (CSCS) is a scheme managed by the National Training Authority FAS. This scheme is backed up by legislation, in particular, the Safety Health and Welfare at work (construction) Regulations 2006 Schedule 4. The regulations list tasks which are common to the construction industry. If a task is listed in the schedule then you must hold a CSCS card to carry out this task on a construction project. A large amount of underground services are located under roads (including footways, cycletracks, roadways etc). Carrying out construction work  on or near a roadway  brings additional hazards, the most obvious being live traffic. The Safety Health and Welfare at work (Construction) (Amendment No. 2)Regulations 2008 (S.I. No. 423 of 2008) sets out the requirements for protecting workers and the public  when working on roads.  Below are some of the CSCS tasks which will be common in relation to avoiding dangers from underground services.

14.5.1 Locating of Underground Services.

The Safety Health and Welfare at Work (Construction) Regulations 2006  requires persons carrying out the task of Locating Underground Services to be in possession of a CSCS card for this task. Contractors must ensure that before excavation begins that underground services are located. This task and the methods involved are dealt with in detail in Section 8 relating to Cable and pipe-locating devices. The person carrying out this task must be in possession of the CSCS card. For further information on this course contact FAS on 1800 611 116 or log onto www.fas.ie

14.5.2 Assisting in the implementation of  Health and Safety at Roadworks (CSCS)

When construction works on roads are in progress you must have a person on site who has been issued with a valid construction skills registration card relating to Assisting health and safety at roadworks. The works must also be supervised by a competent person who has been issued with a valid construction skills registration card relating to signing, lighting and guarding on roads which is further dealt with below. In general this relates to work which doesn’t  interfere with the roadway traffic.

14.5.3 Signing, Lighting and Guarding (CSCS)

Where any construction work which obstructs the roadway (part of road where vehicles travel) or where pedestrians, people with disabilities or cyclists are diverted onto the roadway due to construction work, there must be on that site at all times when road signing, lighting and guarding is being installed, modified or removed, at least one person who has been issued with a valid construction skills registration card relating to signing, lighting and guarding on roads. In general this relates to works which interfere with the roadway traffic.

Further Information

For further information please refer to Guide to the Safety, Health and Welfare at Work (Construction)(Amendment No. 2) Regulations 2008 (S.I No. 423 of 2008)

15.0 Notes on Appendices

Appendices (i) to (iii) give advice on matters relating to each of the four main types of underground services (gas, electricity, sewerage and water). This is additional information and should be read and used in conjunction with the advice contained in the main text.

Appendix 4 gives a suggested job aid for workers on a safe system of work for digging.

APPENDICES

Appendix 1:	Electricity cables

Appendix 2:	Gas pipes

Appendix 3:	Water pipes and sewers

Appendix 4:	Suggested job aid for workers on a safe system of work for digging

Appendix 1:	Electricity cables

Plans

A1.1  The  electricity  service  providers  should  be  consulted  wherever  possible  and  all relevant plans obtained. (Note: While most electricity cables are owned by the ESB, many underground cables are the property of local authorities and are used for the provision of services such as public lighting, traffic lights and so on. Other underground cables may be the property of public bodies or private companies).

A1.2 The representation of underground cables on plans may vary depending on the density  of  the  underground  networks  (i.e.  the  number  of  cables  running  in  close proximity), the scale of the plans and local historical recording conventions. Advice for interpretation  should  be  sought  from  the  issuing  office.  It  should  be  noted  that low/medium voltage cables and high-voltage cables may be shown on separate plans.

Cable-locating devices

A1.3 While hum detectors (e.g. cable-locating devices set on power mode) are the easiest devices to use, they do not respond to unloaded or direct current cables. Furthermore, they may fail to detect lightly loaded low-voltage cables (such as those used for street lighting) and well-balanced high-voltage cables.  A   locator   with   a   radio   frequency detection mode may detect these cables and, therefore, should be used for additional back-up checks.

A1.4 Even where a locating device does not give a positive reading, there may still be cables present and these may still be live.

A1.5 If a cable that is recorded on a plan cannot be located, appropriate assistance or advice should be sought. If digging has to start before such assistance or advice has been obtained, extreme care should be taken.

Safe digging practice

A1.6 In the vast majority of cases there will be no permanent surface markers or other visible signs to indicate the presence of a buried cable. Even if no cables are shown on plans or detected by a locator, a close watch should be kept for any signs that might indicate their presence.

A1.7 Underground cables are normally laid in trenches between 400mm and 1m deep. However, depths should never be assumed. Cables are often found just below the surface.

As a result, therefore, even shallow excavations may present a source of danger. This factor should always be borne in mind, particularly if the ground has been disturbed or if there are cellars or other structures such as bridges in the area, which may have prevented cables being laid at standard depths.

A1.8 Cables may have been laid in any of a number of different ways – directly in the ground with a bed or surround of fine soil or sand; in earthenware or concrete pipes; in pitch-filled

cast iron formers, or in plastic pipes or ducts. Occasionally they may be encased in steel pipes,

or a covering of tiles, bricks, slabs, timber boards or coloured plastic marker tape may be laid above them. However, such coverings may have been disturbed and moved subsequently and, therefore, should not be relied upon to give an accurate indication of cable position. These factors further emphasise the importance of using safe digging practice.

A1.9 During digging work, a careful watch should be kept for evidence of cables and repeat checks should be made with a locator to determine more precisely the position of any cable. It should be noted that a cable should be considered positively located only after it has been safely exposed. Even then, digging should proceed with care, as there may

be other cables, particularly high-voltage cables, nearby or lower down.

A1.10 Occasionally, cables are terminated in the ground by means of a seal, or some other form of external mechanical protection.	These  ‘pot-ended’  or  ‘bottle-ended’  cables should always be treated as live and should not be assumed to be abandoned or disused. They may be difficult to detect with locators even when live.

A1.11 When joints on electricity cables are encountered, they should be treated with extreme care. The joints may be enclosed in cast iron or earthenware casings, or in plastic casings.  They  need  proper  support  and  should  never  be  disturbed,  except  following consultation and agreement with the utility or service provider.

A1.12  The  use  of  hand-held  power  tools  to  break  up  paved  surfaces  often  leads  to accidents. Where practicable, such power tools should not be used within 0.5m of the indicated line of a cable buried in or below a hard surface. Where power tools have been used to break away the surface from the indicated line of the cable, it should then be positively located by careful hand digging under the hard surface. The material under the hard surface should be removed gradually until the cable is exposed.   If the cable is not exposed, then it must be assumed to be embedded in the hard surface. Where possible, a cable locator should be used as a depth guide down the side of the excavation.

The 0.5m safety margin may be reduced:

(a)	where congestion of buried cables renders it impracticable; or

(b)	where surface obstructions limit the space available; but only if the line of the cable has been positively identified by plans and confirmed by a locator.

Because it may be difficult to confirm depth, hand-held power tools should never be used over the cable unless either:

(a)	the cable has already been exposed by digging under the surface to be broken out and is at a safe depth, (at least 300mm) below the bottom of the hard surface material; or

(b)	physical precautions have been taken to prevent the tool striking the cable.

Advice on the safe use of hand tools is given in Section 9.

A1.13 Excavating close to electricity cables buried in concrete is dangerous. For this reason alone electricity cables should not be buried in concrete and the utility or service providers should ensure that their own employees and contractors are aware that this practice is unacceptable.

A1.14 Using mechanical means to break up concrete can cause damage to cables. If the

cable is live, anyone present is likely to be injured.

A1.15 Alternative routes should be carefully considered as a means of avoiding cables that are buried in concrete.

A1.16 Where it is necessary to break away or disturb the concrete in which a cable is embedded, either the utility or service provider should be asked to disconnect it from supply, or an alternative safe method of excavation should be agreed with the utility or service provider before excavation work begins. It is important to note that the use of powered hand tools close to cables is likely to represent the greatest risk of injury.

A1.17  Where  a  buried  cable  has  been  disconnected  from  supply  to  allow  for  safe excavation, it is essential that liaison should be maintained between the parties involved

to ensure that the work has been completed and that workmen have cleared the site before the cable is reconnected.

A1.18 Where mechanical excavators are being used in an area likely to be in the vicinity

of underground cables, the work should be arranged in such a way as to ensure that damage to cables is avoided. In addition, all personnel should be kept well clear of the excavator bucket while digging work is going on.

Drivers should be instructed to remain in the cab if a cable is struck. If the driver has to leave the cab, he or she should jump clear of the machine rather than climb down, to avoid the risk of electrocution. A designated person should be assigned to guard the excavator and ensure that no person enters the area or touches either the excavator or the cable until the utility or services provider has made the damaged cable safe.

A1.19 The most common injuries resulting from cable accidents are flash burns, splatter burns from molten metal or ignited oil and electrical burns. If electrical cables are likely

to be encountered during excavation work, employers should take into consideration in their  risk  assessments  whether  the  work  merits  issuing  personnel  with  either  flame- retardant clothing, or clothing designed to protect against an electric arc. Advice on the suitability  and  performance  of  personal  protective  clothing  should  be  sought  from reputable companies that specialise in this area.

A1.20 Accidents sometimes occur after underground cables have been exposed. Cables should not be used as handholds or footholds by anyone climbing in and out of the trench. Where a cable that is exposed for more than one metre crosses a trench, support should

be provided. If the exposed length is less than one metre, support should still be considered

if joints have been exposed or if the cable appears otherwise vulnerable to damage. If advice or help is needed, the cable service provider should be contacted.

Suitable  precautions  should  be  taken  to  prevent  damage  from  ongoing  work  in  the excavation area (e.g. by use of physical means such as timber boards or sand bags). Cables that  are  lying  at  the  bottom  of  an  excavation  area  should  be  protected  by  nail-free wooden planks, troughing or some other suitable means. Care should be taken not to use materials or equipment that could damage or penetrate the outer sheath of the cables. Cables  should  not  be  moved  aside  unless  the  operation  is  supervised  by  the  service provider. Precautions should be taken to prevent access to exposed cables by children or other unauthorised personnel.

A1.21 Hard or sharp materials such as pieces of rock, large stones, hard-core or surplus

concrete should not be tipped into open cable trenches. Advice on back-filling cable trenches should be obtained from the cable service provider.	As   a   general   rule,   all exposed cables should be back-filled with a 75mm minimum surround of compacted sand. Disturbed tiles and bricks should be replaced and new warning tape should be placed above the excavated area.

A1.22 Any damage to an electricity cable should be reported immediately to the cable service provider and work should not be undertaken in the vicinity of a damaged cable until the service provider has investigated its condition. (Some cables may automatically

‘trip out’ when damaged, but these may be reconnected after the cable service provider has been notified of the damage).

A1.23 Recommended standards for new underground electricity cable installations on new developments and in existing roads and streets.

Buried electricity cables may be laid either directly in the ground or they may be installed

in impact-resistant ducts or pipes. As a general guideline, new cables should be installed

at depths of approximately 450mm in footpaths and driveways and at greater depths of approximately 600mm when installed in road carriageways or grassed areas.

However, local conditions may dictate that these depths vary, particularly where pipes and cables cross, or where underground structures or other obstructions are crossed. Depths may also vary at entrances to buildings, beside street furniture and at underground link disconnection boxes. Deviation from the recommended standards outlined above should only  occur  if  local  conditions  make  compliance  impracticable.  If  cables  are  buried  at shallower depths than those recommended, then this should be noted on the record drawings.

The clearance in all directions between underground electricity cables and other services should be approximately 300mm. With the exception of crossing points, services should not

be laid above electricity cables. This is because, following installation, continuous access will be required for the repair of faults or the installation of new service connections. These connections are usually jointed live in the case of low-voltage mains cables.

While  there  is  no  agreed  industry  standard  in  Ireland  governing  the  relative  lateral positioning of services in footpaths, general guidance may be found in the UK publication National Joint Utilities Group (NJUG) Guidelines on the Positioning and Colour Coding of Underground Utilities’ Apparatus 2007 Efforts should be made to comply with this standard, or other equivalent standards of good practice for new installations,

in order to minimise the risks that arise from the installation of underground services.

A1.24 Colour marking and strength specification of ducts for underground electricity cables

a)	All new underground ducts laid for the installation of electricity cables of 125V

or greater must be RED and must carry the warning: DANGER ELECTRICITY CABLES. They must also conform to the deformation and impact resistance requirements  and  all  other  requirements  as  set  out  in  the  “Material  34

Specification” in Section A1.25 below.

A1.25   MATERIAL   SPECIFICATION   FOR   RED   uPVC   AND   MDPE   DUCTING   FOR   THE INSTALLATION OF UNDERGROUND ELECTRICITY CABLES

|  | MAINS CABLE DUCT | HOUSE SERVICE CABLE DUCT |
| --- | --- | --- |
| Duct outside diameter (mean) Duct type Duct rating UPVC quality Duct colour – outside Duct deformation requirement Impact resistance Duct minimum wall thickness Duct end; spigot end Circumferential mark on plain pipe end for correct push-in distance Duct ovality including socket Eccentricity of socket relative to duct Duct inner surface | 125.0mm – 125.4mm uPVC, 6m lengths; Spigot and socket type Normal duty per EN 50086 – 2 specification 100% virgin material Red – BS Type 5252 04E53 – 04E56 Must pass EN50086 – 2 <5% deformation requirement for 450N loading on 200mm sample Per 50086 – 2 12 samples; 5kg striker: 570mm fall height:>28 Joules – no crack in at least 9 samples The larger of the two criteria below;: (1) Wall thickness to pass 5% deformation /impact requirement above and (2) Minimum wall thickness of 3.8mm (required for cable pulling) Spigot; : plain end bevelled to allow easy jointing of duct on site, minimum thickness of plain end to be 1.3mm, bevel length 5mm Circumferential mark required to indicate Correct push- in distance for duct jointing for spigot and socket joints. Location: 105mm – 110mm to suit socket length below 2.00mm max None allowed and no angle allowed between socket centre line and the duct longitudinal axis to avoid ripping cable sheath during cable pulling Smooth low friction surface completely free of ripples, sharp edges & protrusions. Friction coefficient <0.28 | 50mm MDPE, 6m straight lengths or 50m coils 750 N – EN50086 – 2 100% virgin material Red as for 125mm Minimum 1mm thickness of colour Must pass EN50086 – 2 - :1996 <5% deformation for 750 N loading on 200mm sample As for 125mm Duct wall thickness based on 750N loading test. Duct ends bevelled to allow jointing of duct on site. Clear circumferential mark required to indicate correct push- in distance for duct jointing using standard 50mm couplers 1.4mm max None As for 125mm ducting Friction coefficient <0.28 |

DUCT MARKING

Legend content:

Repetition rate/gap between legend

Colour of legend, size of lettering

Batch No/name of manufacturer

AND

date of manufacture

Red colour fastness

All bends for 125MM duct

Bend ovality

Couplers for 50mm OD duct

“DANGER ELECTRICITY CABLES”

150mm max gap between adjoining legends

Black

2 X 20mm height i.e. 2 lines of 20mm height @ 180° apart. NOTE: 3 lines of

20mm

6mm minimum lettering size

one year minimum required so as to provide 12-month storage period at builders providers premises

One year outdoor weathering test required or suitable accelerated colourfastness test

All Angles: radius = 1.2m minimum for

22, 45 and 90° material as per pipe specification above. (3.8mm minimum)

2mm max (same as for pipe)

“DANGER ELECTRICITY CABLES”

150mm max gap between adjoining legends

Black

2 X 8mm – 10mm height @ 180° apart

6mm minimum lettering size

one year minimum required so as to provide 12-month storage period at builders providers premises

Slip or rubber gasket type with no internal obstructions/sharp edges. A centring ridge is required that does not protrude.

Appendix 2: Gas pipes

A2.1	GENERAL

Natural gas, which is highly flammable, is transported in a network of polyethylene and steel pipes at pressures ranging from 70 Bar to 20 mBar. Damage to a gas main may result

in large volumes of gas escaping into the atmosphere in an uncontrolled manner. Even if there is no smell of gas, any damage to a gas pipe should be reported regardless of how minor the damage might appear to the naked eye. An immediate repair may prevent an accident at a later stage due to a stress failure at the location of the original minor damage.

Most  underground  gas  pipes  are  the  property  of  gas  transmission  or  distribution companies. One notable exception to this is private ‘metered’ estates, which may have gas piped to users from a bulk liquefied petroleum gas (LPG) tank. In the case of the latter, the service provider should be able to supply the requisite information. Estates that comprise privately  owned  dwellings  do  not  normally  have  a  site  owner  or  manager.  In  such circumstances  information  may  be  obtained  from  the  LPG  supplier  whose  name  and telephone number (manned 24 hours) should be displayed in the bulk storage vessel compound. The risks associated with leaking LPG are even greater than those associated with leaking natural gas as it is heavier than air and does not disperse as readily. In addition, it can travel great distances below ground level before accumulating at low levels.

All personnel who are involved in carrying out work near underground gas plant should observe the specific requirements set out by gas utility companies and should ensure that their staff or representatives may have access to the plant at all times. No unauthorised repairs to gas pipes should be made. If there is any doubt about the need to carry out repairs, the advice of the relevant gas company should be sought.

Natural gas pipeline infrastructure in Ireland may be categorised as follows:

Steel Transmission pipelines operating at internal pressures ranging from 7Bar to 85Bar. PE/steel Distribution pipework operating at internal pressures ranging from 20mBar to 4

Bar.

The following points are relevant to both transmission and distribution:

The promoter of the new works should notify gas pipeline companies before any of the following activities are carried out in the vicinity of existing gas infrastructure:

•  Excavation, which includes any site investigation work such as trial pits or boreholes

•  Use of naked flame – welding or other hot works involving naked flame

•  Use of explosives – before a decision is made to use explosives for blasting within

30m of any part of gas pipeline infrastructure (400m for transmission infrastructure), advice should be sought from the gas pipeline utility companies

• Piling – gas pipeline companies must be consulted before any piling is carried out within 15m of an existing gas pipeline

Plans

On request, the local gas service provider will confirm approximate locations of gas pipes, usually in the form of plans. Early contact, preferably at the planning stage, is beneficial and will allow full discussion of proposals to ensure the safety of plant and operators. Plans do not normally show the position of service connections. Their existence should be assumed and it may be possible to estimate the probable line of the service connection pipe from the gas meter position, or from the point of entry to the premises. Where the presence of gas mains which operate at pressures of 4 Bar (60 psig) and above is indicated, the service provider should be consulted further before work begins.

Pipe locators

Locator devices that use radio frequency detection or transmitter/receiver technology should be used to help locate metallic gas pipes before excavation. However, it should be noted that, increasingly, gas pipes are made of plastic and therefore cannot be traced by such devices. This factor further reinforces the importance of using plans and safe digging practices.

Safe digging practice and avoidance of long-term damage

The depth of cover from gas mains laid in a roadway is normally 750mm. For those laid in

a footway it is 600 mm. The depth of cover for gas service connections is normally 450 mm

in both roadways and footpaths. However, at entry points to buildings, the depth of cover for a service connection may be 375mm. It is important to note that these depths are merely a guide and pipes may be found at shallower levels. For example, pipes such as those passing over cellars or in the vicinity of bridge structures may have been laid at shallower levels, or the depth of cover may have been reduced after the pipe was installed because other work such as road alterations were being carried out in the area.

Gas pipes

Gas pipes are laid directly in the ground although in certain soils selective backfill may have been used as a bed and pipe surround. Ductile iron pipe will sometimes be found wrapped  in  loose  fit  polyethylene  (plastic)  sleeving  as  protection  against  corrosion. Polyethylene mains may be inserted into redundant cast iron or ductile iron gas mains. Marker tiles may be used above gas pipes, e.g. where they have been laid at a shallow depth in bridge structures or above cellars.

Polyethylene mains may have a coloured plastic marker tape above them. The presence of gas plant may also be indicated by valve boxes and marker posts. Marker posts/plates are sometimes  used  to  indicate  the  position  and  size  of  valves  or  siphons  on  gas  mains. However, such markers may have been disturbed and should not be relied upon as an accurate indicator of pipe position.

Plastic gas pipes

Plastic gas pipes should be located by hand digging before mechanical excavation begins.

It may also be necessary to use this method to locate metallic pipes if their position has not already been determined by a pipe-locating device. The use of hand digging is particularly important  for  service  connection  pipes,  which  will  not  be  marked  on  plans.  The recommended method is to dig a trial trench along the road near the kerb, or on the footpath, where the depth of the service connection pipes is likely to be at its shallowest. Once the position and depth of the pipes have been determined, work may proceed.

Gas pipes

Gas pipes may have projections such as valve housings, siphons and stand pipes and these will  not  be  shown  on  the  plans.  In  order  to  allow  for  these  projections,  mechanical excavators should not be used within 0.5m of a gas pipe. However, depending on pipeline pressure, the gas company may advise maintaining even greater safety distances.

Hand-held power tools

Hand-held power tools may damage buried gas pipes and they should be used with care until the exact position of an underground pipe has been determined.

Crossing points

In cases where heavy plant and other machinery may have to cross the line of a gas pipe during construction work, the number of crossing points should be kept to a minimum. These points should be clearly indicated and crossings at other positions along the line of the pipe should be prevented. Where the pipe is not adequately protected by an existing road, crossing points should be suitably reinforced with sleepers, steel plates or a specially constructed reinforced concrete raft. The utility or service provider will advise on the type

of reinforcement necessary.

Explosives

Explosives should not be used within 30m of a gas pipe and piling or vertical boring should not be carried out within 15m of any gas pipe without prior consultation and agreement with the service provider. The service provider should be consulted before carrying out excavation work within 10m of any above-ground gas installation.

Welding

If welding or other hot work involving naked flames is to be carried out close to gas plant and the presence of gas is suspected, the utility or service provider should be asked to carry out atmosphere checks before work begins. Even if the atmosphere is gas-free, care should be taken to ensure that no damage occurs. Particular care should be taken to avoid damage by heat, sparks or naked flames to plastic gas pipes or to the protective coatings

on other gas pipes.

Building in and around gas pipes

No manhole, chamber or other structure should be built over, around or under a gas pipe and no work should be carried out that results in a reduction of cover or protection over

a pipe, without first consulting the utility or service provider.

Excavations near gas pipes

Where gas pipes cross, or are parallel and close to excavations, changes in back-fill may cause differential ground settlement and increased stress in the pipe. Where pipes are parallel  and  close  to  excavations,  the  degree  of  risk  depends  on  the  depth  of  the excavation,  the  distance  of  the  pipe  from  the  excavation  and  the  type  of  soil.  If  an excavation  is  likely  to  affect  support  for  a  gas  pipe,  the  service  provider  should  be consulted. In some cases it may be necessary to divert the gas pipe before work begins.

Use of back-fill during excavation work

If a gas pipe is uncovered during excavation work, the back-fill should be adequately compacted, particularly beneath the pipe itself. This measure is designed to prevent any settlement that could subsequently damage the pipe. The back-fill should comprise fine material or sand and should not contain stones, bricks, lumps of concrete etc. It should be suitably compacted to give comparable support and protection to that provided before excavation. No power compaction should take place until a 200mm cover of selected fine-

fill is in place.

Road construction work

If road construction work is being carried out close to the top of a gas pipe, the service provider should be asked to give directions on specific precautions to be taken.

Use of concrete or other hard material

Concrete or other hard material should never be placed or left under or near any gas pipe

as this could cause pipe fracture at a later date. Concrete back-fill or slabbing should not be used within 300mm of a gas pipe.

Uncovering a gas pipe during excavation

If a gas pipe with a damaged wrapping is uncovered during excavation work, the service provider should be informed so that repairs may be carried out to prevent future corrosion and leakage.

Pipe restraints

Pipe restraints or thrust blocks close to gas mains should never be removed.

In the event of damage to a gas pipe/pipeline, work should cease immediately and the following precautionary measures should be taken:

1.	Report all damage even if there is no smell of gas.

2.	Shut down all working plant in the area near the damaged pipe.

3.	Keep personnel away from the affected area.

4.	Prevent all sources of ignition (e.g. smoking, naked flames etc.).

5.	Do not use mobile phones near the gas leak.

6.	Do not try to repair the damage.

7.	Contact the gas company emergency service (24 hours).

8.	Assistance is to be given to gas company emergency crews as necessary, or as requested, to safeguard both personnel and property.

A2.2	Special considerations for transmission gas pipelines

A2.2.1 General

Transmission gas pipelines may be described as follows:

•	Very high pressure

•	Fully welded steel pipes

•	Generally, size ranges from 150mm to 1metre diameter

•	Pipelines usually have either a sacrificial or an impressed current  cathodic protection system. In addition, the pipeline is coated in yellow and/or encased

in black wrapping.

•	Minimum depth of cover is 1.0m but cover may be less in some cases.

A2.2.2 Locating the transmission pipeline

Before any work is carried out in the vicinity of existing gas pipelines, the gas pipeline company representative should arrange for location and pegging out of the pipeline as well as for the supervision of the digging of any trial holes necessary to confirm the position of the pipe.

A2.2.3 Design considerations for installation of new services close to transmission gas pipelines

l. Orientation and location

Where a new service is to cross either above or below an existing gas pipeline, the normal minimum distance between the outside of the pipeline and the service to be installed should be 600mm.

In special circumstances this distance may be reduced at the discretion of the pipeline

company engineer. At such crossings both the pipeline and the new service should be suitably supported to prevent any future settlement and the back-fill should be packed and consolidated to the satisfaction of the pipeline company engineer (see Section A2.2.5).

As a general rule, no new service should be laid parallel to an existing gas pipeline. However, in special circumstances (e.g. motorways) a new service may be laid parallel to

an existing pipeline provided that there is adequate clearance (normally 600mm) between them and provided that the service is not laid either directly above or below the existing gas pipeline.

2. Cathodic protection

Transmission gas pipelines are cathodically protected. Where a new service is to be laid and

is to be similarly protected, the gas pipeline company is obliged to carry out interaction tests to determine whether its own system is adversely affected.

3. Pressure testing

Hydraulic  testing  should  not  take  place  within  8m  of  an  existing  gas  pipeline  unless precautions have been taken to mitigate the effects of a possible burst. These precautions may include the use of pre-installation tested pipe, sleeving, barriers etc. as directed by the pipeline company engineer.

A2.2.4 Excavation

Where it is necessary to excavate below a transmission gas pipeline, the pipeline must during all stages of the operation be supported to the satisfaction of the engineer. On completion, permanent supports should, if necessary, be constructed to avoid future settlement.

Mechanical excavation by powered tools is not permitted within a distance of 3m and the use  of  hand-held  power-assisted  tools  should  not  be  permitted  within  1.5m  of  a transmission gas pipeline or associated equipment.

Consideration may be given to a relaxation of these limits provided that prior notice is given  to  the  gas  pipeline  company  of  the  excavating  methods  to  be  used  and  the safeguards to be employed.

To avoid damage during construction work, exposed gas pipelines must be protected by cladding (e.g. timber) as directed by the pipeline company engineer.

A2.2.5 Back-filling

Those responsible for the new works should give the gas pipeline company at least 48 hours notice of their intention to back-fill under, over or near an existing transmission pipeline. The gas pipeline company representative must be in attendance during all back-

filling operations and advise on the suitability and degree of consolidation of back-fill

material around the pipeline.

Any damage to the coating of the transmission gas pipeline, even if minor in extent, must

be brought to the notice of the gas pipeline company representative so that necessary repairs may be carried out before back-filling is completed. Any minor damage caused to pipe coating and test leads that has been brought to the attention of the gas pipeline company must be repaired by that company.

A2.2.6 Special operations

Use of explosives: Before a decision is made to use explosives for blasting within 400m of any part of gas pipeline infrastructure, advice must be sought from all relevant gas pipeline companies.

Piling: Gas pipeline companies must be consulted before any piling is carried out within

15m of an existing gas pipeline.

Appendix 3: Water pipes and sewers

The appropriate records office should be contacted and the location of all sewers, water mains,  kiosks,  meters  and  wiring/cable  ducting  should  be  determined  before  any excavation work begins.

The location of mains on drawings should be taken as approximate. In general, if there is

a sewer or water main (diameter is >= 300mm) in the vicinity, then the appropriate service provider engineer should be contacted in order to co-ordinate the excavation work.

Mains runs must be marked out before excavation begins.

During excavation, in addition to the safe digging practice previously outlined in this document, the following precautions should be taken:

a)	If a water main spans a road cutting or similar excavation, then the main must be adequately braced so that no movement takes place.

b)	If a pipe anchor is exposed, then excavation must cease and the appropriate engineer must be contacted.

c)	Fittings (ferrules, air valves and so on) should not be interfered with.

d)	Excavation in vicinity of mains must be carried out by hand in order to avoid damage to the pipe.

If  the  pipe  in  question  is  a  high-pressure  trunk  main,  then  the  following  additional precautions must be adhered to:

1.	No personnel should be positioned inside the trench while the mechanical excavator is operating, in case a high-pressure break occurs.

2.	Continuous inspections are essential in order to determine whether the next excavation level is clear.

3.	If  any  leak  is  discovered,  then  the  service  provider  must  be  contacted immediately and the area sealed off to keep it safe and to prevent members

of the public from gaining access.

Appendix 4 - Suggested job aid for workers on a

safe system of work for digging

26 February 2009

# Text boxes

(Third Edition - December 2007)